SPECIFICATION:

Solid State

Reduced Voltage Motor Starter

MEDIUM VOLTAGE

# Contents

Contents	2

Introduction	3

1.1	Scope	3

1.2	Supplier Qualifications	3

Equipment Specifications	4

2.1	Environmental Specifications	4

2.2	Physical Specifications	4

2.3	General Electrical Specifications	4

2.4	Safety	4

2.5	Low voltage testing and operational simulation	5

Logic Control Configuration	6

3.1	Control Interface	6

3.2	Operating Configurations	6

3.3	Motor and System Protection Features	7

3.4	Programmable Relay Outputs	8

3.5	Inputs	8

3.6	Metering and Performance Monitoring	8

Support and Services	10

4.1	Commissioning	10

4.2	Documentation	10

4.3	Training	11

4.4	Warranty and Repair	11

# Introduction

## Scope

This document specifies the minimum requirements for a solid state reduced voltage motor starter for medium voltage application.

This specification is intended as a guideline for suppliers wishing to supply their product to <customer name> for their <project name/outline of requirement>.

The solid state reduced voltage starter shall control three phases at	V,

Hz and shall be rated for use with AC induction motors of	hp/kW. The starter shall provide soft starting and soft stopping of the motor as required.

## Supplier Qualifications

The equipment shall have been manufactured by a single vendor.

The manufacturer shall be certified under ISO9001:2015.

The manufacturer shall have produced solid state reduced voltage starters for a minimum of 15 years.

The manufacturer shall have a global manufacturing network able to provide 24 hour support.

## Design Requirements

Starters shall be reduced-voltage solid state type.

The motor starters will be constructed as part of floor standing motor control centre.

The starters shall be by the same manufacturer. Controls shall be coordinated to provide proper operation.

All motor starters and controllers shall be designed, manufactured and tested to meet or exceed the requirements of the latest published standard of IEC in addition to local authority requirements. The supplier shall list the standard(s) used.

The starters shall be manufactured in sections, assembled and fully tested on a medium voltage motor at the supplier’s manufacturing facility.

The starters shall be fully retested on site in accordance with the supplier’s approved site acceptance test plan.

The starter manufacturer shall offer full cooperation and liaison with the Contractor for commissioning the connected equipment. The manufacturer shall make available an experienced engineer at site during the commissioning of the plant.

# Equipment Specifications

## Environmental Specifications

The soft starter shall be suitable for storage at temperatures from -25 ºC to +70 ºC.

The soft starter shall be suitable for operation at temperatures from -10 ºC to +60 ºC.

The soft starter shall be suitable for operation at temperatures up to 50 ºC without derating.

The soft starter shall be suitable for operation at altitudes up to 1000 m above sea level without derating.

The soft starter shall be suitable for operation in environments with relative humidity between 5% and 95% (non-condensing).

Printed circuit boards used in the starter must be assembled and conformally coated with silicone or similar approved compound at the supplier’s own facility.

All printed circuit boards shall be individually tested by the supplier during manufacture.

## Physical Specifications

The soft starter shall be suitable for supply in IP00 format.

The soft starter shall be modular in design and construction.

The components for controlling each power phase, including (but not limited to) voltage sensors, SCRs, firing circuits and transformers, shall be assembled into one discrete module per phase.

The power control assemblies shall be suitable for mounting in different configurations, including but not limited to side-by-side horizontal and side-by-side vertical orientations.

The soft starter shall allow the power control assembly for a single phase to be removed without requiring removal or disassembly of the power control assembly for any other phase.

The soft starter shall allow the power control assembly for a single phase to be replaced without requiring replacement of the power control assembly for any other phase.

Replacement of a power control assembly by a qualified service technician shall not take longer than 20 minutes.

## General Electrical Specifications

The soft starter shall be a point on wave controlling type using reverse parallel SCR pairs in the controlled phases of the power section.

The soft starter shall include three current transformers for deriving motor current to ensure accurate motor protection.

The nominal ratings information shall be shown on the nameplate label of the soft starter and shall be shown in AC53b format.

The soft starter control power supply input shall accept either mains supply voltages, 85 to 264 VAC, or 90 to 300 VDC.

## Safety

The soft starter’s low voltage systems, including (but not limited to) the user interface and time-critical processing functions, must be electrically isolated from the medium voltage power section.

The control and power components of the soft starter must be connected by fibre-optic cabling only.

The control input signals shall be current limited.

Control inputs on the soft starter shall be driven by 24 VDC, which must be supplied by the soft starter’s internal power supply.

The soft starter shall be subjected toa  partial discharge test during manufacture, at the supplier’s manufacturing facility.

## Low voltage testing and operational simulation

The equipment shall provide means to safely test its correct installation:

The equipment shall provide a means to test the installation using a low voltage motor

The equipment shall provide a means to test operation of all control circuitry and protection mechanisms, without connection to medium voltage. Functions to be tested include, at minimum:

operation of main contactor relay

operation of bypass contactor relay

firing signals are sent and received on each phase (tested individually)

correct operation of bypass readback input

motor starting

motor stopping

protection activation

The equipment shall provide a means to safely test the correct operation of current-based protections, by secondary injection.

# Logic Control Configuration

## Control Interface

The equipment shall be supplied with a separate user interface specifically designed for operation in conjunction with the equipment.

Operating feedback and fault diagnostic information shall be displayed in clear language on the user interface. The exclusive use of fault codes is not acceptable.

The equipment shall allow the user to select the language for feedback messages.

The equipment must support feedback in at least the following languages: Brazilian Portuguese, Chinese, English, French, German, Italian, Russian, Spanish.

The user interface shall comprise, at minimum:

A four line, 16 character, backlit LCD screen for information feedback in selected language and have the ability to display data captured by the soft starter in a graphical format

status LEDs indicating

motor state

starter control state

trip status

output relay activity

local pushbuttons to control:

motor start

motor stop

starter reset

menu access

parameter configuration

The user interface shall provide a means for an operator to quickly access and configure parameters.

The equipment shall permit the operator to save the current configuration to an internal file.

The equipment shall permit the operator to reload a previously saved configuration set from an internal file.

The equipment shall include a function to restore default settings.

The user interface shall display the software version(s) used within the soft starter.

The equipment shall support remote management via a control network.

The equipment shall provide an on-board real-time clock.

The user interface shall permit the user to select four operating conditions to be displayed simultaneously on one viewing screen.

The user interface shall provide a graphical means of reviewing motor performance.

## Operating Configurations

The equipment shall be suitable for use with dual-speed motors. The equipment shall be suitable for use with slip-ring motors.

The soft starter shall provide, at minimum, the following starting methods:

Current ramp starting

Constant current starting

Kickstart

Full voltage (direct on-line) starting with active motor protections

Full voltage (direct on-line) starting without protections (for emergency)

The soft starter shall provide timed voltage ramp stopping of the motor.

The equipment shall provide a means of automatically stopping the motor at a predetermined time.

The equipment shall provide a means of automatically stopping the motor after a predetermined period of operation.

## Motor and System Protection Features

The equipment shall provide the following protections as standard:

Excess start time

Motor overload

Motor thermistor

Current imbalance

Frequency

Phase sequence

Instantaneous overcurrent

Power loss

Undercurrent

Motor not detected

Starter communications

Network communications

Overvoltage

Undervoltage

Ground fault

EEPROM failure

Bypass contactor failure

L1 phase loss

L2 phase loss

L3 phase loss

L1 shorted SCR

L2 shorted SCR

L3 shorted SCR

Time-Overcurrent

SCR overtemperature

Battery / clock failure

Internal communication failure

Current reading error

Gate drive failure

Conduction 1 invalid

Conduction 2 invalid

Conduction 3 invalid

Assembly power low

The equipment's sensitivity to protection situations shall be programmable.

The equipment's response to a protection activation shall be selectable. The equipment's possible responses to a protection activation shall include, at minimum:

trip: cease operation and disable the motor

warn: notify the condition to the operator and continue operating

ride through: write the event to memory

The speed of the equipment’s response to protection situations shall be programmable.

The equipment’s behaviour for each protection situation shall be fully independent of other protections.

## Relay Outputs (fixed and programmable)

The equipment shall provide output relays to control operation of:

main contactor

bypass contactor

slip-ring changeover contactor

power factor correction contactor

The equipment shall provide an output relay to indicate that the unit is operating.

The soft starter shall provide programmable on and off delay times for each of the two programmable relay outputs.

The equipment shall provide at least three additional relays with user-selectable functionality, enabling indication of:

Low current state

High current state

Motor temperature state

Trip states:

Current imbalance

Ground fault

Heatsink overtemperature

Instantaneous overcurrent

Mains frequency

Motor overload

Motor thermistor

Phase loss

Undercurrent

Undervoltage

## Inputs (fixed and programmble)

The soft starter shall provide at least six fixed inputs with the following functionality:

- Remote start signal

- Remote stop signal

- Remote reset signal

- Bypass feedback

- Power supply feedback

- Full voltage (direct on-line) operation

The soft starter shall provide at least two programmable inputs permitting auxiliary trip functionality. Each such input must be configurable for normally closed or normally open operation. It must be possible to identify the activation of each such input via configurable messages on the user interface.

The settings for each programmable input shall be fully independent of the other.

## Metering and Performance Monitoring

The equipment shall include comprehensive metering and monitoring functions.

The equipment shall provide real-time feedback of operating conditions, including:

average current

L1 current

L2 current

L3 current

average voltage

L1 voltage

L2 voltage

L3 voltage

mains frequency

motor real power consumption

motor apparent power consumption

motor power factor

elapsed running time

time to run before programmed stop (when running)

Output of frequency locked derived (virtual) phase 1-neutral zero crossing signal

Internal variable Phase 1 conduction period

Internal variable Half cycle count (ie MV supply period)

Internal variable Lag count (ie time difference between derived phase 1 voltage zero crossing and end of conduction.)

The equipment shall provide feedback of historical operating information, including:

lifetime hours run

lifetime start count

resettable hours run

resettable start count

resettable kWh count

The equipment shall record full details of its state at the time of every protection activation. The recorded details shall include, at minimum:

time stamp

protection type

motor operating status

mains frequency

line current

line voltage

The equipment's protection log shall store no fewer than eight trips.

The equipment shall record all changes to its configuration.

The equipment's change log shall store no fewer than 99 events.

The soft starter shall have a built-in diagnostic board.

Diagnostic data shall be recorded:

- During a start: From the time the Start command is given to the time the starter enters the running state.

- During a stop: From the time the Stop command is given to the time the starter exits the stopping state.

The supplier shall supply a software tool to configure, monitor and troubleshoot the soft starter. Software tool shall have a trending feature where up to six signals can be displayed in real time.

The software tool shall have a multilevel access feature for configuration of parameter settings.

# Support and Services

## Commissioning

The equipment supplier shall assist the customer in commissioning the equipment.

The equipment supplier shall provide suitably trained staff to ensure successful commissioning.

Commissioning support staff shall have been trained at the supplier’s manufacturing facility and shall be available from major regional locations worldwide.

The supplier shall support a comprehensive site test to verify the input and output current, voltage, frequency, power factor, acceleration and deceleration rate etc.

The supplier’ trained representative shall conduct all tests on site.

The Owner’s representative shall be invited to witness all tests on site.

Upon completion of site tests a duly signed report listing all tests and checks, together with all supporting documents and drawings where applicable, shall be submitted for review.

## Documentation

The equipment shall be provided with a complete set of supporting documentation, including:

General documentation

Company profile, history and structure

Proof of company legal and financial status

Company quality policies and certifications

Reference list and testimonials from relevant previous installations

Technical documentation

Manufacturing schedule

Electrical drawings

Mechanical general assembly drawings

Single line diagrams

Technical datasheet

Calculation guidelines and recommendations for fuse selection

Calculation guidelines and recommendations for power factor correction

Calculation guidelines and recommendations for transformers

Calculation guidelines and recommendations for cables

Detailed calculation record for successful starting configuration

Detailed calculation record for successful stopping configuration

Detailed calculation record for heat dissipation

Parameter list

Soft starter user manual

User manual for communications option (if fitted)

List of recommended spare parts

List of and specifications for required special tools

Bill of quantities

Inspection documentation

Manufacturing quality control plan

Inspection and test plan

Factory acceptance test plan

Site acceptance test plan

Product approval certificates (standards testing and compliance)

Manufacturing calibration certificates

## Training

The equipment supplier shall provide a complete training schedule with the equipment.

The equipment supplier shall undertake to deliver the complete training programme if required by the customer.

The training programme shall be delivered at the customer's premises or at the supplier's premises, as required by the customer.

The training programme shall deliver to the customer the skills to:

appropriately program the equipment to meet customer requirements

safely commission the equipment

safely operate the equipment

identify and rectify operating problems caused by incorrect programming

identify and diagnose operating problems caused by faulty equipment

The supplier must also be prepared to provide training on:

Theory of operation

Layout and component level study

Hands-on training on assembly & configuration of the soft starter

Installation & commissioning procedures

Hands-on training on trouble shooting and working with various components

Routine maintenance practices

Spare part ordering & inventory control

## Warranty and Repair

The supplier shall guarantee the equipment against faults of materials or manufacture workmanship for a period of not less than 18 months.

The supplier shall guarantee to provide servicing support for the equipment for a period of not less than 10 years from date of supply.

## Standards and Approvals

The soft starter shall be designed and materials shall be furnished in accordance with the latest revisions of applicable sections of the following codes and standards.

EN 50178:1998	Electronic equipment for use in power installation

GB3906	AC metal enclosed switchgear

IEC 60068-2-6-Fc	Environmental testing – 
Part 2-6: Tests – Test Fc: Vibration (sinusoidal)

IEC 60071-1	Insulation coordination – 
Part 1: Definitions, principles and rules

IEC 60071-2	Insulation coordination – Part 2: Application guide

IEC 60073	Basic and safety principles for man-machine interface, marking and identification – 
Coding principles for indicators and actuators

IEC 60270	High-voltage test techniques – Partial discharge measurements

IEC 60282-1	High voltage fuses – Part 1: Current-limiting fuses

IEC 60529	Degrees of protection provided by enclosures (IP Code)

IEC 60947-4-2	Low-voltage switchgear and controlgear – 
Part 4-2: Contactors and motor-starters – 
AC semiconductor motor controllers and starters

IEC 60747-5-5	Semiconductor devices - Discrete devices - Part 5-5: Optoelectronicdevices - Photocouplers

IEC 61000-6-2	Electromagnetic compatibility (EMC) – 
Part 6-2: Generic standards – Immunity for industrial environments

IEC 61000-6-4	Electromagnetic compatibility (EMC) – 
Part 6-4: Generic standards – Emission standard for industrial environments

IEC 61869-1	Instrument transformers – Part 1: General requirements

IEC 62271-1	High Voltage control gear and switchgear – 
Part 1: Common specifications

IEC 62271-100	High Voltage control gear and switchgear – 
Part 100: High voltage alternating current circuit breakers

IEC 62271-102	High Voltage control gear and switchgear – 
Part 102: Alternating current disconnectors and earthing switches

IEC 62271-105	High Voltage control gear and switchgear – 
Part 105: Alternating current switch-fuse combinations

IEC 62271-106	High Voltage control gear and switchgear – 
Part 106: Alternating current contactors, contactor-based controllers and motor starters

IEC 62271-200	High Voltage control gear and switchgear – 
Part 200: AC metal-enclosed switchgear and control gear for rated voltages above 1 kV and up to 5 kV